Spec. No.: SFA-MFC

Version No.:2013001

规格承认书

Specification for approval

产品名称：MFC系列 6.35*32mm快断型 玻璃管保险丝

Product Type: MFC Series 6.35*32mm Fast-Acting Glass Tube Fuse

瑞卓电子(东莞)有限公司

Dongguan Reomax Electronics Co., LTD

电话: +86-769-85634648 传真: +86-769-85635648

厂址: 广东省东莞市大岭山镇地塘岭工业园20号

网址: http://www.reomaxfuse.com

瑞卓电子(香港)有限公司

Reomax Electronics (HK) Limited

Add: 5th Floor, Bright way tower, No.33 Mong kok road, Kowloon Hong Kong

Web: http://www.reomaxfuses.com

目录Contents

1.	适用范围 / Scope of Application	3

2.	安规认证标准及编号 / Standards and Agency Approvals	3

3.	产品标示 / Product Marking	4

4.	外观及形状 / Appearances and Configuration	5

5.	结构及尺寸 / Dimensions and Structure	5

6.	材料明细 / Material Details	6

7.	产品特性 / Product Characteristics	6

8.	电气特性 / Electrical Characteristics	6

9.	环境特性 / Environmental Characteristic	9

10.	安装建议 / Installation Recommendations	9

11.	包装 / Packaging	11

12.	其他 / Others	12

附件I: 安规证书 / Appendix I: Safety approval certificates	12

- 适用范围 / Scope of Application

本产品适用于各类电子设备电路的过流保护作用, 广泛应用于照明设备、电源设备以及适配器等领域。

This product is suitable for various kinds of electronic devices’ circuit over current protection. Widely used in industrial of Lighting, Power supply and Adapter applications, etc.

- 安规认证标准及编号 / Standards and Agency Approvals

2.1执行标准：遵循UL 248 -1 / -14。

Standards：In accordance with UL 248 -1 / -14.

2.2认证范围 Certification：

| 额定电压 Voltage Rating | 安规标准 Agency | 认证范围 Ampere Range | 证书编号 Agency File Number |
| --- | --- | --- | --- |
| 125V/250V | UL | 100mA ~ 30A | Pending |
|  | C-UL | 100mA ~ 30A | Pending |
|  | PSE | 100mA ~ 30A | Pending |
|  | KTL | 100mA ~ 30A | Pending |

2.3目录编号 Catalogue No.，A=250V / B=125V，● 已认证Approved / ○ 认证中Pending

| 目录编号 Catalog No. | 额定电流 Ampere Rating | 额定电压 Voltage Rating | 分断能力 Breaking Capacity | 熔化热能 I2TMelting Integral(A2.S) | 安规认证 Agency Approvals |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MFC0100A/B | 100mA | 250V/125V | 10000A@125 V AC (100mA~10A); 35A@250V AC (100mA~1A); 100A@250V AC (1.25A~3.5A); 200A@250V AC (4A~10A). | 0.003 | ○ | ○ | ○ | ○ |
| MFC0160A/B | 160mA | 250V/125V |  | 0.008 | ○ | ○ | ○ | ○ |
| MFC0200A/B | 200mA | 250V/125V |  | 0.02 | ○ | ○ | ○ | ○ |
| MFC0250A/B | 250mA | 250V/125V |  | 0.026 | ○ | ○ | ○ | ○ |
| MFC0300A/B | 300mA | 250V/125V |  | 0.047 | ○ | ○ | ○ | ○ |
| MFC0315A/B | 315mA | 250V/125V |  | 0.055 | ○ | ○ | ○ | ○ |
| MFC0350A/B | 350mA | 250V/125V |  | 0.072 | ○ | ○ | ○ | ○ |
| MFC0400A/B | 400mA | 250V/125V |  | 0.10 | ○ | ○ | ○ | ○ |
| MFC0500A/B | 500mA | 250V/125V |  | 0.16 | ○ | ○ | ○ | ○ |
| MFC0630A/B | 630mA | 250V/125V |  | 0.28 | ○ | ○ | ○ | ○ |
| MFC0750A/B | 750mA | 250V/125V |  | 0.49 | ○ | ○ | ○ | ○ |
| MFC0800A/B | 800mA | 250V/125V |  | 0.60 | ○ | ○ | ○ | ○ |
| MFC1100A/B | 1A | 250V/125V |  | 0.8 | ○ | ○ | ○ | ○ |
| MFC1125A/B | 1.25A | 250V/125V |  | 1.6 | ○ | ○ | ○ | ○ |
| MFC1150A/B | 1.5A | 250V/125V |  | 2.5 | ○ | ○ | ○ | ○ |
| MFC1160A/B | 1.6A | 250V/125V |  | 3.2 | ○ | ○ | ○ | ○ |
| MFC1200A/B | 2A | 250V/125V |  | 5.6 | ○ | ○ | ○ | ○ |
| MFC1250A/B | 2.5A | 250V/125V |  | 7.6 | ○ | ○ | ○ | ○ |
| MFC1300A/B | 3A | 250V/125V |  | 14 | ○ | ○ | ○ | ○ |
| MFC1315A/B | 3.15A | 250V/125V |  | 19 | ○ | ○ | ○ | ○ |
| MFC1350A/B | 3.5A | 250V/125V |  | 20 | ○ | ○ | ○ | ○ |
| MFC1400A/B | 4A | 250V/125V |  | 25 | ○ | ○ | ○ | ○ |
| MFC1500A/B | 5A | 250V/125V |  | 42 | ○ | ○ | ○ | ○ |
| MFC1600A/B | 6A | 250V/125V |  | 80 | ○ | ○ | ○ | ○ |
| MFC1630A/B | 6.3A | 250V/125V |  | 96 | ○ | ○ | ○ | ○ |
| MFC1800A/B | 8A | 250V/125V |  | 200 | ○ | ○ | ○ | ○ |
| MFC2100A/B | 10A | 250V/125V |  | 320 | ○ | ○ | ○ | ○ |
| MFC2120A/B | 12A | 250V/125V |  | 470 | ○ | ○ | ○ | ○ |
| MFC2150A/B | 15A | 250V/125V |  | 650 | ○ | ○ | ○ | ○ |
| MFC2200A/B | 20A | 250V/125V |  | 870 | ○ | ○ | ○ | ○ |
| MFC2250A/B | 25A | 250V/125V |  | 1320 | ○ | ○ | ○ | ○ |
| MFC2300A/B | 30A | 250V/125V |  | 1820 | ○ | ○ | ○ | ○ |

- 产品标示 / Product Marking

保险丝两端铜帽上需有下列标示。

The fuses cap shall have the following markings.

示例Example:

|  | MFC | 1A | 250V |  |
| --- | --- | --- | --- | --- |
| ① | ② | ③ | ④ | ⑤ |

| ① | 制造厂商标识/Reomax Trade Mark: |
| --- | --- |
| ② | 系列型号名称/Series Type Name: MFC (快断型/Fast-Acting) |
| ③ | 额定电流/Rated Current (A): A 或or mA |
| ④ | 额定电压/Rated Voltage (V): 125V/250V |
| ⑤ | 认证符号/ Approval Marks: |

注意 / Note：对于标示的大小和位置没有规定。

Size and position of the markings shall not be provided.

- 外观及形状 / Appearances and Configuration

4.1 外观不应出现显著的污点、裂纹，标识应该容易辨识。

There shall not be any remarkable stain and crack on the appearances, markings shall be easily legible.

4.2 形状：带直线引脚小型玻璃管保险丝。

Configuration：Axial Leaded Miniature Glass Tube Fuse.

- 结构及尺寸 / Dimensions and Structure

单位：毫米 / Unit: mm

- 材料明细 / Material Details

| 编 号 NO. | 零 件 名 称 Part Name | 材 质 Material |
| --- | --- | --- |
|  | 铜帽 Cap | 黄铜镀镍 Nickel Plated Brass |
|  | 玻璃管 Body | 玻璃管 Glass Tube |
|  | 熔丝 Fuse element | 合金 Alloy |
| ④ | 引线 Lead wire | 镀锡铜线 Tin Plated Copper |

- 产品特性 / Product Characteristics

7.1 引脚拉力强度 / Lead Pull Strength

5牛顿 10±1 秒 / 5N for 10±1 Seconds

7.2 引脚推力强度 / Lead Thrust Strength

2 牛顿10±1 秒 / 2N for 10±1 Seconds

7.3 可焊性 / Solder ability

波峰焊/Wave : 260℃，≤3s;

烙铁焊/Soldering Iron: 350±10℃，≤3s.

7.4 耐焊接热 / Soldering Heat Resistance

波峰焊/Wave : 260℃，10s;

烙铁焊/Soldering Iron: 350℃，5s.

- 电气特性 / Electrical Characteristics

8.1 实验条件：Test Condition

所有测试环境温度为25±5℃。

All electrical test is to be conducted with the ambient air at a temperature of 25±5℃.

8.2 负载能力 / Load capacity：

当保险丝通过100%的额定电流时，在4小时内不应熔断。

When the fuse loads through 100% of rated current, should blow within 4 hours.

8.3 分断能力 / Interrupting Rating：

保险丝承受分断能力：

10000安培使用125伏交流电源(MFC对应额定电流In范围100mA~10A)；

35安培使用250伏交流电源(MFC对应额定电流In范围100mA~1A)；

100安培使用250伏交流电源(MFC对应额定电流In范围1.25A~3.5A)；

200安培使用250伏交流电源(MFC对应额定电流In范围4A~10A)。

Breaking Capacity:

10000A at125 V AC (MFC In range 100mA~10A);

35A at 250V AC (MFC In range 100mA~1A);

100A at 250V AC (MFC In range 1.25A~3.5A);

200A at 250V AC (MFC In range 4A~10A).

8.4 温度上升试验 / Rising Temperature Test：

通1.0倍额定电流，当温度稳定时（5分钟测量4次，且每次测量值与平均值相差不超过2℃）。测得熔断体任何部位的温升不得超过75℃，周围环境温度为25±5℃。

When the 100% times of Ampere Rating passes the fuse, after reaching thermal balance , the temperature on the fuse surface rising shall not be higher than 75℃. Note: Rising temperature = the Surface temperature - Ambient temperature.

8.5熔断时限 / Operating Characteristics

| 额定电流的% % of Ampere Rating(In) | 熔断时间 Blowing Time |
| --- | --- |
| 100%* In | 大于4小时(4 hours Min) |
| 135%* In | 小于1小时(1 hour Max) |
| 200%* In | 小于5秒(5 sec Max) |

8.6 平均时间电流曲线图 / Average Time Current Curves

时间(秒) / TIME IN SECONDS

电流(安培) / CURRENT IN AMPERES

- 环境特性 / Environmental Characteristic

9.1　使用温度范围 / Operating Temperature

-55℃～+125℃。

9.2　保存条件 Stock Condition

湿度：相对湿度≦75%平均可以存放3年。

Humidity：Relative humidity ≤ 75% store 3 years in average.

9.3  若操作环境温度超出25±5℃范围，在选用保险丝规格时，需考虑操作环境温度对保险丝的影响，请参照如下：温度-电流曲线图。

When choosing the fuse's specification, if the operating environmental temperature beyond the scope from 20~30℃, engineer should consider the environmental temperature's affection to fuses. Please refer: Temperature Rerating Curve:

- 安装建议 / Installation Recommendations

10.1 建议按照如下示意图方式进行安装。

Propose installation way as following picture.

A、卧式安装

Horizontal installation

B、立式安装

Vertical installation

C、立式安装

Vertical installation

10.2 建议焊接参数 / Recommended Soldering Parameters

- 波峰焊参数 / Wave Parameters:

锡炉温度 / Solder Pot Temperature: 260℃ Max

焊接时间 / Solder Dwell Time: 2~5s

- 手工焊参数 / Hand-Solder Parameters:

烙铁温度 / Solder Iron Temperature: 350±5℃

焊接时间 / Heating Time: 5s Max

- 包装 / Packaging

11.1 包装袋/盒印明下列标示: / The following items indicated on the label:

产品料号、额定(电压、电流)、分断类型及安规名称。

Catalog number, ratings (voltage, current), interrupting type and safety mark.

包装材料均符合RoHS/REACH/HF的环保要求， 且包装材料不会和零件发生化学反应，造成不良。

The packing material conforms to ROHS/REACH/HF environmental protection request. And the packing materials will not have the chemical reaction with the components.

11.2 包装数量 / Packing Quantity

每胶袋200个保险丝 / Bulk 200 pcs in per poly bag;

每10胶袋1个内盒 / 10 poly bags in per inner box;

每4个内盒1个外箱 / 4 inner boxes in per outer carton

11.3 包装箱尺寸 / Packing Size

单位：毫米 / Unit: mm

| A. 内盒Inner box： | B. 外箱Outer carton： |
| --- | --- |
| L240±2 * W170±2 * H110±2 | L390±5 * W240±5 * H250±5 |

- 其他 / Others

12.1 如果在使用中有超出本规格书的要求，须经双方协商确认。

In the event that an impropriety is found beyond this specification, it shall be fixed by mutual agreement between the parties.

12.2 如果本规格书有不适当的情况，须通过双方协商并由本公司修改。

In the event that an impropriety is found in this specification, REOMAX ELECTRONICS CO., LTD. shall amend it by mutual agreement between the parties.

# 附件I: 安规证书 / Appendix I: Safety approval certificates